## Cover Page
Year: | 2025
Notes
As per clause 5.13.3 of the NER, this System Limitation Report includes the required information as per the template published by the AER

## System Limitation Report
Year | 2025
Asset Name | Bairnsdale (BDL) | Benalla (BN) | Bayswater (BWR) | Clyde North (CLN) | Doreen (DRN) | Epping (EPG) | Kinglake (KLK) | Kalkallo (KLO) | Kilmore South (KMS) | Lang Lang (LLG) | Lilydale (LDL) | Maffra (MFA) | Mansfield (MSD) | Myrtleford (MYT) | Newmerella (NLA) | Officer (OFR) | Pakenham (PHM) | Seymour (SMR) | Thomastown (TT) | Traralgon (TGN) | Watsonia (WT) | Wangaratta (WN) | Warragul (WGL) | Wonthaggi (WGI) | Woori Yallok (WYK) | Wodonga Terminal Station (WOTS) | Benalla 11 Feeder | Benalla 24 Feeder | Berwick North 12 feeder | Bayswater 22 Feeder | Clyde North 11 Feeder | Clyde North 13 Feeder | Clyde North 14 Feeder | Clyde North 21 Feeder | Clyde North 22 Feeder | Clyde North 23 Feeder | Cranbourne 21 Feeder | Cranbourne 23 Feeder | Cranbourne 31 Feeder | Cranbourne 33 Feeder | Doreen 11 Feeder | Eltham 21 Feeder | Epping 12 Feeder | Epping 13 Feeder | Epping 21 Feeder | Epping 23 Feeder | Epping 31 Feeder | Epping 32 Feeder | Epping 33 Feeder | Epping 35 Feeder | Hampton Park 22 Feeder | Hampton Park 23 Feeder | Hampton park 24 Feeder | Kalkallo 14 Feeder | Kakllo 24 Feeder | Kilmore South 12 Feeder | Moe 23 Feeder | Mansfield 4 Feeder | Officer 11 Feeder | Officer 14 Feeder | Officer 21 Feeder | Pakenham 21 Feeder | Pakenham 22 Feeder | Pakenham 32 Feeder | Seymour 24 Feeder | Traralgon 31 Feeder | Traralgon 11 Feeder | Waragul 13 Feeder | Waragul 21 Feeder | Wangarrata 2 feeder | Wangarrata 4 Feeder | Wangarata 6 Feeder | Wodonga Terminal Station 11 Feeder | Wodonga Terminal Station 25 Feeder
Asset Abbreviation | BDL | BN | BWR | CLN | DRN | EPG | KLK | KLO | KMS | LLG | LDL | MFA | MSD | MYT | NLA | OFR | PHM | SMR | TT | TGN | WT | WN | WGL | WGI | WYK | WOTS | bn11 | bn24 | bwn12 | bwr22 | cln11 | cln13 | cln14 | cln21 | cln22 | cln23 | cre21 | cre23 | cre31 | cre33 | drn11 | elm21 | epg12 | epg13 | epg21 | epg23 | epg31 | epg32 | epg33 | epg35 | hpk22 | hpk23 | hpk24 | klo14 | klo24 | kms12 | moe23 | msd4 | ofr11 | ofr14 | ofr21 | phm21 | phm22 | phm32 | smr24 | tgn31 | tgn11 | wgl13 | wgl21 | wn2 | wn4 | wn6 | wots11 | wots25
Asset Name & Type | Bairnsdale (BDL) ZSS | Benalla (BN) ZSS | Bayswater (BWR) ZSS | Clyde North (CLN) ZSS | Doreen (DRN) ZSS | Epping (EPG) ZSS | Kinglake (KLK) ZSS | Kalkallo (KLO) ZSS | Kilmore South (KMS) ZSS | Lang Lang (LLG) ZSS | Lilydale (LDL) ZSS | Maffra (MFA) ZSS | Mansfield (MSD) ZSS | Myrtleford (MYT) ZSS | Newmerella (NLA) ZSS | Officer (OFR) ZSS | Pakenham (PHM) ZSS | Seymour (SMR) ZSS | Thomastown (TT) ZSS | Traralgon (TGN) ZSS | Watsonia (WT) ZSS | Wangaratta (WN) ZSS | Warragul (WGL) ZSS | Wonthaggi (WGI) ZSS | Woori Yallok (WYK) | Wodonga Terminal Station (WOTS) TS | Benalla 11 Feeder | Benalla 24 Feeder | Berwick North 12 feeder | Bayswater 22 Feeder | Clyde North 11 Feeder | Clyde North 13 Feeder | Clyde North 14 Feeder | Clyde North 21 Feeder | Clyde North 22 Feeder | Clyde North 23 Feeder | Cranbourne 21 Feeder | Cranbourne 23 Feeder | Cranbourne 31 Feeder | Cranbourne 33 Feeder | Doreen 11 Feeder | Eltham 21 Feeder | Epping 12 Feeder | Epping 13 Feeder | Epping 21 Feeder | Epping 23 Feeder | Epping 31 Feeder | Epping 32 Feeder | Epping 33 Feeder | Epping 35 Feeder | Hampton Park 22 Feeder | Hampton Park 23 Feeder | Hampton park 24 Feeder | Kalkallo 14 Feeder | Kakllo 24 Feeder | Kilmore South 12 Feeder | Moe 23 Feeder | Mansfield 4 Feeder | Officer 11 Feeder | Officer 14 Feeder | Officer 21 Feeder | Pakenham 21 Feeder | Pakenham 22 Feeder | Pakenham 32 Feeder | Seymour 24 Feeder | Traralgon 31 Feeder | Traralgon 11 Feeder | Waragul 13 Feeder | Waragul 21 Feeder | Wangarrata 2 feeder | Wangarrata 4 Feeder | Wangarata 6 Feeder | Wodonga Terminal Station 11 Feeder | Wodonga Terminal Station 25 Feeder
Constraint primary driver | Safety | Asset Condition | Asset Condition | Capacity | Reliability | Reliability | Safety | Capacity | Asset Condition | Reliability | Safety | Asset Condition | Reliability | Reliability | Reliability | Reliability | Reliability | Safety | Asset Condition | Asset Condition | Asset Condition | Reliability | Asset Condition | Reliability | Reliability | Reliability | Reliability | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity
Location of constraint (start) | -37.80837, 147.64766 | -36.55601, 145.96176 | -37.83473, 145.27189 | -38.09483, 145.33297 | -37.60524, 145.13389 | -37.65253, 145.02631 | -37.51517, 145.31635 | -37.538614529,144.940788225 | -37.31799, 144.97194 | -38.26753, 145.55641 | -37.76354, 145.35806 | -37.97089, 146.9821 | -37.05044, 146.07123 | -36.56539, 146.70302 | -37.73931, 148.42519 | -38.051720237,145.444574095 | -38.07079, 145.49419 | -37.03603, 145.15452 | -37.69088, 145.01077 | -38.18926, 146.56011 | -37.71335, 145.08575 | -36.36455, 146.31435 | -38.154092261,145.942734283 | -38.59392, 145.60978 | -38.59392, 145.60978 | -38.59392, 145.60978 | -36.55601, 145.96176 | -36.55601, 145.96176 | -38.01373, 145.34771 | -37.83473, 145.27189 | -38.09483, 145.33297 | -38.09483, 145.33297 | -38.09483, 145.33297 | -38.09483, 145.33297 | -38.09483, 145.33297 | -38.09483, 145.33297 | -38.08074, 145.26328 | -38.08074, 145.26328 | -38.08074, 145.26328 | -38.08074, 145.26328 | -37.60524, 145.13389 | -37.71667, 145.13865 | -37.65253, 145.02631 | -37.65253, 145.02631 | -37.65253, 145.02631 | -37.65253, 145.02631 | -37.65253, 145.02631 | -37.65253, 145.02631 | -37.65253, 145.02631 | -37.65253, 145.02631 | -38.03588, 145.26667 | -38.03588, 145.26667 | -38.03588, 145.26667 | -37.538614529,144.940788225 | -37.538614529,144.940788225 | -37.31799, 144.97194 | -38.17063, 146.25615 | -37.05044, 146.07123 | -38.051720237,145.444574095 | -38.051720237,145.444574095 | -38.051720237,145.444574095 | -38.07079, 145.49419 | -38.07079, 145.49419 | -38.07079, 145.49419 | -37.03603, 145.15452 | -38.18926, 146.56011 | -38.18926, 146.56011 | -38.154092261,145.942734283 | -38.154092261,145.942734283 | -36.36455, 146.31435 | -36.36455, 146.31435 | -36.36455, 146.31435 | -36.15494, 146.94987 | -36.15494, 146.94987
Location of constraint (end) | -37.80837, 147.64766 | -36.55601, 145.96176 | -37.83473, 145.27189 | -38.09483, 145.33297 | -37.60524, 145.13389 | -37.65253, 145.02631 | -37.51517, 145.31635 | -37.538614529,144.940788225 | -37.31799, 144.97194 | -38.26753, 145.55641 | -37.76354, 145.35806 | -37.97089, 146.9821 | -37.05044, 146.07123 | -36.56539, 146.70302 | -37.73931, 148.42519 | -38.051720237,145.444574095 | -38.07079, 145.49419 | -37.03603, 145.15452 | -37.69088, 145.01077 | -38.18926, 146.56011 | -37.71335, 145.08575 | -36.36455, 146.31435 | -38.154092261,145.942734283 | -38.59392, 145.60978 | -38.59392, 145.60978 | -38.59392, 145.60978 | -36.540304249,145.999261944 | -36.241308517,145.793488866 | -38.045834836,145.345186142 | -37.852370028,145.282714277 | -38.179960466,145.314168084 | -38.130339940,145.303652550 | -38.039346967,145.329286573 | -38.047689115,145.322971293 | -38.105468751,145.397150451 | -38.072282647,145.365417272 | -38.130134821,145.229839806 | -38.052960205,145.301307947 | -38.124506015,145.248200010 | -38.222699770,145.337018486 | -37.603477230,145.061038658 | -37.709564635,145.171084686 | -37.607251593,145.000713442 | -37.576173007,145.031972997 | -37.637764777,144.973507425 | -37.632718984,144.976498983 | -37.659639636,144.992780026 | -37.549149618,145.031938261 | -37.651614216,144.976451400 | -37.645358097,144.995039351 | -38.036632828,145.322496753 | -38.085869152,145.258819285 | -38.006712901,145.273495031 | -37.488206992,145.148428998 | -37.380607553,145.001188319 | -37.415342870,145.023662030 | -38.184011172,146.309506876 | -38.243565017,146.410455003 | -38.040404326,145.370751925 | -38.059512546,145.340629913 | -38.059512546,145.340629913 | -38.089924156,145.506485504 | -38.182223536,145.479856688 | -38.083662342,145.450742887 | -38.183202024,146.468051003 | -38.194185255,146.531495795 | -38.183202024,146.468051003 | -38.111053983,145.771701006 | -38.298594863,145.900101953 | -36.012637137,146.401242319 | -36.426516339,146.243364822 | -36.672466995,146.262835982 | -36.537565161,147.053392651 | -36.249447862,146.805947046
Asset ID | BDL | BN | BWR | CLN | DRN | EPG | KLK | KLO | KMS | LLG | LDL | MFA | MSD | MYT | NLA | OFR | PHM | SMR | TT | TGN | WT | WN | WGL | WGI | WYK | WOTS | bn11 | bn24 | bwn12 | bwr22 | cln11 | cln13 | cln14 | cln21 | cln22 | cln23 | cre21 | cre23 | cre31 | cre33 | drn11 | elm21 | epg12 | epg13 | epg21 | epg23 | epg31 | epg32 | epg33 | epg35 | hpk22 | hpk23 | hpk24 | klo14 | klo24 | kms12 | moe23 | msd4 | ofr11 | ofr14 | ofr21 | phm21 | phm22 | phm32 | smr24 | tgn31 | tgn11 | wgl13 | wgl21 | wn2 | wn4 | wn6 | wots11 | wots25
Network Element | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Zone Substation | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder | Feeder
Residential customers affected | 24965 | 12708 | 18046 | 44846 | 30545 | 32118 | 2523 | 19951 | 7007 | 7295 | 21976 | 8937 | 7021 | 6169 | 4054 | 24997 | 16854 | 11509 | 15022 | 18823 | 24412 | 18628 | 26894 | 22388 | 22388 | 22388 | 4756 | 1119 | 1322 | 1108 | 11720 | 4691 | 6144 | 5988 | 3388 | 5096 | 5204 | 3321 | 6340 | 4785 | 5988 | 2457 | 7079 | 7480 | 227 | 1667 | 3219 | 3996 | 296 | 316 | 4770 | 3587 | 1581 | 11401 | 8438 | 4833 | 2455 | 3058 | 5940 | 3650 | 4545 | 2159 | 1685 | 3446 | 3727 | 2237 | 4402 | 4188 | 5182 | 3922 | 2855 | 4597 | 3864 | 3766
Residential customers affected | 3.041% | 1.548% | 2.198% | 5.463% | 3.721% | 3.913% | 0.3074% | 2.431% | 0.8536% | 0.8887% | 2.677% | 1.089% | 0.8553% | 0.7515% | 0.4939% | 3.045% | 2.053% | 1.402% | 1.83% | 2.293% | 2.974% | 2.269% | 3.276% | 2.727% | 2.727% | 2.727% | 0.5794% | 0.1363% | 0.1611% | 0.135% | 1.428% | 0.5715% | 0.7485% | 0.7295% | 0.4127% | 0.6208% | 0.634% | 0.4046% | 0.7724% | 0.5829% | 0.7295% | 0.2993% | 0.8624% | 0.9113% | 0.02765% | 0.2031% | 0.3922% | 0.4868% | 0.03606% | 0.0385% | 0.5811% | 0.437% | 0.1926% | 1.389% | 1.028% | 0.5888% | 0.2991% | 0.3725% | 0.7236% | 0.4447% | 0.5537% | 0.263% | 0.2053% | 0.4198% | 0.454% | 0.2725% | 0.5363% | 0.5102% | 0.6313% | 0.4778% | 0.3478% | 0.56% | 0.4707% | 0.4588%
Asset rating Nameplate (MVA) 2026 | 81 | 40.5 | 81 | 99 | 66 | 99 | 10 | 66 | 30 | 33 | 99 | 40.5 | 26 | 20 | 10 | 66 | 66 | 66 | 84 | 60 | 109 | 66 | 84 | 40.5 | 66 | 70.4 | 10.86 | 12.0031 | 11.8888 | 10.2884 | 14.2894 | 13.1082 | 12.3842 | 12.9557 | 14.2894 | 13.1082 | 14.2894 | 13.7178 | 16.2709 | 12.7652 | 12.4223 | 9.8311 | 12.9557 | 13.9084 | 14.7467 | 13.7178 | 9.5263 | 10.86 | 14.7467 | 13.3368 | 12.308 | 12.5747 | 12.0412 | 14.518 | 14.518 | 14.2894 | 6.8589 | 8.7642 | 13.7178 | 13.7178 | 14.2894 | 12.7652 | 14.2894 | 13.1463 | 13.3368 | 6.8589 | 10.6694 | 12.3842 | 13.9084 | 10.86 | 8.0402 | 10.86 | 11.0505 | 9.9073
Asset rating Nameplate (MVA) 2027 | 81 | 40.5 | 81 | 99 | 66 | 99 | 10 | 66 | 30 | 33 | 99 | 40.5 | 26 | 20 | 10 | 66 | 66 | 66 | 84 | 60 | 109 | 66 | 84 | 40.5 | 66 | 70.4 | 10.86 | 12.0031 | 11.8888 | 10.2884 | 14.2894 | 13.1082 | 12.3842 | 12.9557 | 14.2894 | 13.1082 | 14.2894 | 13.7178 | 16.2709 | 12.7652 | 12.4223 | 9.8311 | 12.9557 | 13.9084 | 14.7467 | 13.7178 | 9.5263 | 10.86 | 14.7467 | 13.3368 | 12.308 | 12.5747 | 12.0412 | 14.518 | 14.518 | 14.2894 | 6.8589 | 8.7642 | 13.7178 | 13.7178 | 14.2894 | 12.7652 | 14.2894 | 13.1463 | 13.3368 | 6.8589 | 10.6694 | 12.3842 | 13.9084 | 10.86 | 8.0402 | 10.86 | 11.0505 | 9.9073
Asset rating Nameplate (MVA) 2028 | 81 | 40.5 | 81 | 99 | 66 | 99 | 10 | 66 | 30 | 33 | 99 | 40.5 | 26 | 20 | 10 | 66 | 66 | 66 | 84 | 60 | 109 | 66 | 84 | 40.5 | 66 | 70.4 | 10.86 | 12.0031 | 11.8888 | 10.2884 | 14.2894 | 13.1082 | 12.3842 | 12.9557 | 14.2894 | 13.1082 | 14.2894 | 13.7178 | 16.2709 | 12.7652 | 12.4223 | 9.8311 | 12.9557 | 13.9084 | 14.7467 | 13.7178 | 9.5263 | 10.86 | 14.7467 | 13.3368 | 12.308 | 12.5747 | 12.0412 | 14.518 | 14.518 | 14.2894 | 6.8589 | 8.7642 | 13.7178 | 13.7178 | 14.2894 | 12.7652 | 14.2894 | 13.1463 | 13.3368 | 6.8589 | 10.6694 | 12.3842 | 13.9084 | 10.86 | 8.0402 | 10.86 | 11.0505 | 9.9073
Asset rating Nameplate (MVA) 2029 | 81 | 40.5 | 81 | 99 | 66 | 99 | 10 | 66 | 30 | 33 | 99 | 40.5 | 26 | 20 | 10 | 66 | 66 | 66 | 84 | 60 | 109 | 66 | 84 | 40.5 | 66 | 70.4 | 10.86 | 12.0031 | 11.8888 | 10.2884 | 14.2894 | 13.1082 | 12.3842 | 12.9557 | 14.2894 | 13.1082 | 14.2894 | 13.7178 | 16.2709 | 12.7652 | 12.4223 | 9.8311 | 12.9557 | 13.9084 | 14.7467 | 13.7178 | 9.5263 | 10.86 | 14.7467 | 13.3368 | 12.308 | 12.5747 | 12.0412 | 14.518 | 14.518 | 14.2894 | 6.8589 | 8.7642 | 13.7178 | 13.7178 | 14.2894 | 12.7652 | 14.2894 | 13.1463 | 13.3368 | 6.8589 | 10.6694 | 12.3842 | 13.9084 | 10.86 | 8.0402 | 10.86 | 11.0505 | 9.9073
Asset rating Nameplate (MVA) 2030 | 81 | 40.5 | 81 | 99 | 66 | 99 | 10 | 66 | 30 | 33 | 99 | 40.5 | 26 | 20 | 10 | 66 | 66 | 66 | 84 | 60 | 109 | 66 | 84 | 40.5 | 66 | 70.4 | 10.86 | 12.0031 | 11.8888 | 10.2884 | 14.2894 | 13.1082 | 12.3842 | 12.9557 | 14.2894 | 13.1082 | 14.2894 | 13.7178 | 16.2709 | 12.7652 | 12.4223 | 9.8311 | 12.9557 | 13.9084 | 14.7467 | 13.7178 | 9.5263 | 10.86 | 14.7467 | 13.3368 | 12.308 | 12.5747 | 12.0412 | 14.518 | 14.518 | 14.2894 | 6.8589 | 8.7642 | 13.7178 | 13.7178 | 14.2894 | 12.7652 | 14.2894 | 13.1463 | 13.3368 | 6.8589 | 10.6694 | 12.3842 | 13.9084 | 10.86 | 8.0402 | 10.86 | 11.0505 | 9.9073
Asset rating Nameplate (MW) 2026 | 79.38 | 40.095 | 79.38 | 99 | 66 | 99 | 9.4 | 65.34 | 29.4 | 32.67 | 98.01 | 40.5 | 26 | 20 | 9.7 | 66 | 66 | 66 | 84 | 59.4 | 107.91 | 65.34 | 83.16 | 40.095 | 66 | 70.4 | 10.7514 | 11.523 | 11.7699 | 9.8768 | 14.2894 | 13.1082 | 12.3842 | 12.9557 | 14.1465 | 13.1082 | 14.2894 | 13.5807 | 16.2709 | 12.7652 | 12.4223 | 9.7328 | 12.9557 | 13.9084 | 14.5992 | 13.5807 | 9.431 | 10.86 | 14.1568 | 12.9367 | 12.1849 | 12.4489 | 11.9208 | 14.518 | 14.518 | 14.2894 | 6.7217 | 8.7642 | 13.7178 | 13.7178 | 14.2894 | 12.5099 | 13.8607 | 13.0148 | 13.3368 | 6.7903 | 10.6694 | 12.3842 | 13.9084 | 10.86 | 7.9598 | 10.86 | 11.0505 | 9.9073
Asset rating Nameplate (MW) 2027 | 79.38 | 40.095 | 79.38 | 99 | 66 | 99 | 9.4 | 65.34 | 29.4 | 32.67 | 98.01 | 40.5 | 26 | 20 | 9.7 | 66 | 66 | 66 | 84 | 59.4 | 107.91 | 65.34 | 83.16 | 40.095 | 66 | 70.4 | 10.7514 | 11.523 | 11.7699 | 9.8768 | 14.2894 | 13.1082 | 12.3842 | 12.9557 | 14.1465 | 13.1082 | 14.2894 | 13.5807 | 16.2709 | 12.7652 | 12.4223 | 9.7328 | 12.9557 | 13.9084 | 14.5992 | 13.5807 | 9.431 | 10.86 | 14.1568 | 12.9367 | 12.1849 | 12.4489 | 11.9208 | 14.518 | 14.518 | 14.2894 | 6.7217 | 8.7642 | 13.7178 | 13.7178 | 14.2894 | 12.5099 | 13.8607 | 13.0148 | 13.3368 | 6.7903 | 10.6694 | 12.3842 | 13.9084 | 10.86 | 7.9598 | 10.86 | 11.0505 | 9.9073
Asset rating Nameplate (MW) 2028 | 79.38 | 40.095 | 79.38 | 99 | 66 | 99 | 9.4 | 65.34 | 29.4 | 32.67 | 98.01 | 40.5 | 26 | 20 | 9.7 | 66 | 66 | 66 | 84 | 59.4 | 107.91 | 65.34 | 83.16 | 40.095 | 66 | 70.4 | 10.7514 | 11.523 | 11.7699 | 9.8768 | 14.2894 | 13.1082 | 12.3842 | 12.9557 | 14.1465 | 13.1082 | 14.2894 | 13.5807 | 16.2709 | 12.7652 | 12.4223 | 9.7328 | 12.9557 | 13.9084 | 14.5992 | 13.5807 | 9.431 | 10.86 | 14.1568 | 12.9367 | 12.1849 | 12.4489 | 11.9208 | 14.518 | 14.518 | 14.2894 | 6.7217 | 8.7642 | 13.7178 | 13.7178 | 14.2894 | 12.5099 | 13.8607 | 13.0148 | 13.3368 | 6.7903 | 10.6694 | 12.3842 | 13.9084 | 10.86 | 7.9598 | 10.86 | 11.0505 | 9.9073
Asset rating Nameplate (MW) 2029 | 79.38 | 40.095 | 79.38 | 99 | 66 | 99 | 9.4 | 65.34 | 29.4 | 32.67 | 98.01 | 40.5 | 26 | 20 | 9.7 | 66 | 66 | 66 | 84 | 59.4 | 107.91 | 65.34 | 83.16 | 40.095 | 66 | 70.4 | 10.7514 | 11.523 | 11.7699 | 9.8768 | 14.2894 | 13.1082 | 12.3842 | 12.9557 | 14.1465 | 13.1082 | 14.2894 | 13.5807 | 16.2709 | 12.7652 | 12.4223 | 9.7328 | 12.9557 | 13.9084 | 14.5992 | 13.5807 | 9.431 | 10.86 | 14.1568 | 12.9367 | 12.1849 | 12.4489 | 11.9208 | 14.518 | 14.518 | 14.2894 | 6.7217 | 8.7642 | 13.7178 | 13.7178 | 14.2894 | 12.5099 | 13.8607 | 13.0148 | 13.3368 | 6.7903 | 10.6694 | 12.3842 | 13.9084 | 10.86 | 7.9598 | 10.86 | 11.0505 | 9.9073
Asset rating Nameplate (MW) 2030 | 79.38 | 40.095 | 79.38 | 99 | 66 | 99 | 9.4 | 65.34 | 29.4 | 32.67 | 98.01 | 40.5 | 26 | 20 | 9.7 | 66 | 66 | 66 | 84 | 59.4 | 107.91 | 65.34 | 83.16 | 40.095 | 66 | 70.4 | 10.7514 | 11.523 | 11.7699 | 9.8768 | 14.2894 | 13.1082 | 12.3842 | 12.9557 | 14.1465 | 13.1082 | 14.2894 | 13.5807 | 16.2709 | 12.7652 | 12.4223 | 9.7328 | 12.9557 | 13.9084 | 14.5992 | 13.5807 | 9.431 | 10.86 | 14.1568 | 12.9367 | 12.1849 | 12.4489 | 11.9208 | 14.518 | 14.518 | 14.2894 | 6.7217 | 8.7642 | 13.7178 | 13.7178 | 14.2894 | 12.5099 | 13.8607 | 13.0148 | 13.3368 | 6.7903 | 10.6694 | 12.3842 | 13.9084 | 10.86 | 7.9598 | 10.86 | 11.0505 | 9.9073
Forecast Demand 2026 10% POE (MVA) | 62.6913 | 44.7798 | 62.771 | 124.2514 | 74.8521 | 118.5447 | 6.6618 | 94.1984 | 20.3887 | 33.0834 | 72.4067 | 32.0938 | 20.3389 | 16.7614 | 8.4118 | 76.597 | 79.8845 | 41.6976 | 82.7816 | 49.3469 | 74.7899 | 57.7347 | 87.2604 | 54.6012 | 34.7031 | 41.8699 | 13.8168 | 14.5194 | 14.3585 | 13.5219 | 27.0018 | 17.1356 | 14.3183 | 13.9293 | 17.4873 | 13.6077 | 15.4966 | 17.1449 | 16.4464 | 15.223 | 13.2644 | 10.9147 | 16.0804 | 24.8097 | 16.33 | 13.4467 | 10.8949 | 11.1968 | 16.4511 | 16.4298 | 12.4166 | 12.9376 | 13.5078 | 29.8793 | 25.6895 | 14.3351 | 7.8793 | 9.2387 | 12.6208 | 18.714 | 15.7583 | 25.1398 | 19.1414 | 14.8618 | 15.2566 | 6.9653 | 10.59 | 16.8958 | 17.1679 | 11.5225 | 9.4086 | 11.2093 | 11.695 | 12.5072
Forecast Demand 2027 10% POE (MVA) | 63.7176 | 44.6237 | 63.4216 | 128.0364 | 74.9606 | 121.4869 | 6.6468 | 102.4436 | 20.7499 | 33.0249 | 72.5996 | 32.1259 | 20.2914 | 16.7295 | 8.461 | 81.5678 | 79.6008 | 41.5127 | 82.7373 | 52.5248 | 74.5453 | 57.3784 | 89.446 | 54.4983 | 34.3264 | 42.5889 | 13.8168 | 14.4284 | 14.3413 | 13.8745 | 29.7944 | 17.9696 | 14.6169 | 14.0591 | 18.0025 | 14.5007 | 15.5496 | 16.9975 | 16.792 | 15.7131 | 13.3425 | 10.914 | 16.4811 | 26.075 | 21.096 | 15.7298 | 10.8578 | 11.5451 | 17.9198 | 17.2257 | 12.4559 | 12.9039 | 13.5229 | 34.1265 | 27.3804 | 14.6504 | 7.889 | 9.2223 | 14.0665 | 20.9628 | 15.8624 | 25.1228 | 19.6634 | 14.8174 | 15.2137 | 7.0646 | 10.6929 | 17.4874 | 17.2788 | 11.5427 | 9.3196 | 11.2192 | 12.1823 | 12.8659
Forecast Demand 2028 10% POE (MVA) | 64.1347 | 45.3215 | 64.3028 | 131.3686 | 75.3455 | 119.8786 | 6.663 | 118.3247 | 21.1538 | 33.0633 | 72.6892 | 32.2551 | 20.2507 | 16.7673 | 8.5169 | 84.5283 | 79.5894 | 41.4114 | 83.1283 | 52.415 | 74.2988 | 58.2051 | 94.8495 | 54.5247 | 34.0788 | 42.5369 | 13.7643 | 14.355 | 14.3553 | 14.2752 | 32.8405 | 18.789 | 14.9604 | 14.1989 | 18.5701 | 15.3485 | 21.1974 | 16.8726 | 17.2539 | 16.4149 | 13.4031 | 10.9507 | 17.0233 | 27.3676 | 24.627 | 16.6197 | 10.8323 | 11.9739 | 19.4767 | 18.5976 | 12.4562 | 12.8904 | 13.5549 | 45.8931 | 29.1732 | 15.079 | 7.8788 | 9.257 | 15.4985 | 22.6913 | 16.0331 | 24.8511 | 21.5597 | 14.8012 | 15.1816 | 7.1743 | 10.8425 | 22.1191 | 17.4055 | 11.5772 | 9.2684 | 11.2033 | 12.6449 | 13.1452
Forecast Demand 2029 10% POE (MVA) | 64.8329 | 44.8211 | 65.7114 | 136.7682 | 75.8529 | 121.9204 | 6.7397 | 126.3487 | 21.4292 | 33.1822 | 73.9142 | 32.6072 | 20.3293 | 16.8847 | 8.6257 | 86.8984 | 80.0199 | 41.7033 | 84.734 | 52.7059 | 75.0519 | 57.7579 | 95.1314 | 54.7136 | 34.1141 | 43.1408 | 13.8609 | 14.3612 | 14.4587 | 14.9183 | 36.3853 | 19.6776 | 15.3502 | 14.435 | 19.2299 | 16.4204 | 21.2436 | 16.8153 | 17.6146 | 17.1309 | 13.561 | 11.0416 | 17.5277 | 28.8001 | 28.0728 | 18.2666 | 10.8024 | 12.3835 | 20.9732 | 19.8368 | 12.5778 | 12.8989 | 13.6582 | 50.2549 | 30.9738 | 15.4822 | 7.9155 | 9.3115 | 17.0047 | 23.7065 | 16.3638 | 24.9877 | 21.6659 | 14.8203 | 15.1657 | 7.3174 | 10.9741 | 22.0357 | 17.6669 | 11.707 | 9.2749 | 11.2847 | 13.2213 | 13.5851
Forecast Demand 2030 10% POE (MVA) | 65.9652 | 45.2785 | 70.6007 | 141.634 | 77.0208 | 124.6444 | 6.8596 | 135.5692 | 21.6537 | 33.5865 | 76.1573 | 34.0628 | 20.4863 | 17.1864 | 8.9222 | 88.8048 | 81.1895 | 42.7147 | 88.1963 | 53.0951 | 76.0297 | 59.0498 | 97.2315 | 55.0965 | 34.6881 | 44.2401 | 13.965 | 15.1077 | 14.9616 | 16.2837 | 39.1913 | 20.7903 | 15.7305 | 14.6965 | 19.9231 | 17.4408 | 21.4085 | 16.7632 | 18.1619 | 18.0108 | 13.7564 | 11.1795 | 18.0764 | 30.2174 | 31.4219 | 19.8993 | 10.8117 | 12.8241 | 22.3441 | 21.058 | 12.7541 | 12.9553 | 14.0724 | 55.9901 | 32.9336 | 16.1282 | 8.0959 | 9.3689 | 18.6227 | 24.0253 | 16.6244 | 26.1653 | 21.6119 | 14.9539 | 15.1891 | 7.5283 | 11.1848 | 22.0149 | 17.9495 | 11.8632 | 9.4259 | 11.323 | 13.8637 | 14.0123
Forecast Demand 2026 50% POE (MVA) | 55.6977 | 40.9765 | 55.6569 | 108.3435 | 64.8074 | 101.6723 | 5.8473 | 77.9353 | 19.2203 | 30.4575 | 64.9561 | 28.9453 | 17.2373 | 13.9843 | 8.0408 | 68.9791 | 74.1527 | 37.143 | 75.5604 | 44.2313 | 64.4939 | 51.2244 | 79.5304 | 44.9185 | 30.7665 | 37.7094 | 12.7196 | 13.739 | 13.1389 | 12.6063 | 21.747 | 14.6145 | 12.4548 | 12.7859 | 16.0598 | 10.251 | 13.7375 | 16.1631 | 14.1259 | 13.4893 | 11.606 | 8.716 | 13.5407 | 22.4024 | 12.7205 | 12.0468 | 9.4706 | 8.6452 | 13.3734 | 15.5829 | 10.8275 | 11.8364 | 11.8776 | 25.2995 | 22.6808 | 12.6985 | 6.7874 | 7.8466 | 9.5061 | 16.6805 | 13.6559 | 24.3771 | 18.4188 | 12.8348 | 13.9217 | 6.5355 | 9.1351 | 15.7484 | 15.5156 | 10.3291 | 8.3646 | 10.0058 | 10.216 | 10.8021
Forecast Demand 2027 50% POE (MVA) | 56.7187 | 40.7659 | 55.9729 | 111.4611 | 64.4918 | 104.4042 | 5.9096 | 84.7194 | 19.6688 | 30.4247 | 65.5906 | 29.2257 | 17.1909 | 13.8965 | 8.0852 | 74.0072 | 73.9998 | 37.1166 | 75.9343 | 47.3573 | 64.5142 | 50.84 | 81.7767 | 44.7661 | 30.6124 | 38.0299 | 12.6788 | 13.6331 | 13.0926 | 13.1075 | 24.5067 | 15.372 | 12.7299 | 12.8648 | 16.4602 | 10.8988 | 13.782 | 16.0086 | 14.4563 | 13.9214 | 11.6321 | 8.7369 | 13.9185 | 23.5885 | 17.0125 | 14.5676 | 9.4116 | 8.9551 | 14.7463 | 16.2005 | 10.7578 | 11.7794 | 11.929 | 29.3274 | 24.2143 | 12.9884 | 6.7606 | 7.8299 | 10.9367 | 18.9219 | 13.7668 | 24.3509 | 19.2617 | 12.8056 | 13.9021 | 6.6322 | 9.1803 | 16.4136 | 15.6128 | 10.3196 | 8.3826 | 9.991 | 10.6445 | 11.0668
Forecast Demand 2028 50% POE (MVA) | 56.8612 | 40.9244 | 57.2524 | 115.2173 | 64.501 | 102.6031 | 5.9008 | 99.6669 | 20.1039 | 30.3952 | 65.7044 | 29.003 | 17.2767 | 13.963 | 8.1407 | 76.6284 | 73.965 | 36.8817 | 75.4202 | 47.3776 | 64.6271 | 50.7693 | 87.0476 | 44.911 | 30.4603 | 38.3363 | 12.7416 | 13.7258 | 13.0413 | 13.4969 | 27.2562 | 16.1765 | 13.0604 | 13.0447 | 16.9784 | 11.6921 | 19.3094 | 15.9172 | 14.7349 | 14.4121 | 11.7183 | 8.8185 | 14.415 | 24.694 | 20.1677 | 15.3586 | 9.3645 | 9.2472 | 16.2344 | 17.4759 | 10.865 | 11.7268 | 11.8489 | 40.0999 | 25.6998 | 13.3677 | 6.7562 | 7.803 | 12.2666 | 20.6773 | 13.9037 | 24.6149 | 20.5779 | 12.7829 | 13.8693 | 6.736 | 9.2913 | 21.0391 | 15.7601 | 10.3248 | 8.2588 | 10.0197 | 11.085 | 11.438
Forecast Demand 2029 50% POE (MVA) | 57.1154 | 41.1178 | 58.6272 | 119.0984 | 64.973 | 105.5757 | 5.9489 | 106.8624 | 20.4077 | 30.8677 | 66.6306 | 30.0735 | 17.3524 | 14.0369 | 8.276 | 78.9811 | 74.4648 | 37.1956 | 77.012 | 47.5917 | 65.1344 | 51.1846 | 87.4675 | 44.9706 | 30.4336 | 38.9966 | 12.7483 | 13.8344 | 13.1673 | 14.6054 | 30.0067 | 17.0262 | 13.4429 | 13.1681 | 17.5833 | 12.4587 | 19.3701 | 15.8375 | 15.0401 | 15.1138 | 11.9001 | 8.8454 | 14.8035 | 25.9455 | 23.2525 | 16.6194 | 9.3372 | 9.6034 | 17.6383 | 18.6671 | 10.9348 | 11.7634 | 12.3146 | 43.8359 | 27.3813 | 13.7363 | 6.7921 | 7.8414 | 13.7227 | 21.6109 | 14.0561 | 24.9706 | 20.5696 | 12.8416 | 13.8693 | 6.8745 | 9.4244 | 20.9673 | 15.9167 | 10.4322 | 8.2478 | 10.0619 | 11.5641 | 11.7046
Forecast Demand 2030 50% POE (MVA) | 58.87 | 41.2737 | 61.8783 | 123.2461 | 65.1637 | 106.371 | 6.0885 | 115.5707 | 20.4896 | 31.5616 | 68.1839 | 32.3185 | 17.5414 | 14.3041 | 8.5781 | 80.4506 | 75.0153 | 37.8757 | 80.381 | 48.0728 | 66.2656 | 52.9058 | 90.2362 | 45.1615 | 30.6516 | 40.1266 | 12.9999 | 14.2781 | 13.5629 | 15.2707 | 32.5722 | 17.8251 | 13.7623 | 13.387 | 18.1665 | 13.4205 | 19.5174 | 15.7913 | 15.4191 | 15.8525 | 12.0389 | 8.9552 | 15.3211 | 27.2421 | 26.3316 | 18.252 | 9.3836 | 9.9586 | 18.9224 | 19.9327 | 11.0994 | 11.7346 | 12.1578 | 50.2651 | 29.1508 | 14.261 | 6.8331 | 7.9822 | 15.2322 | 21.9368 | 14.2567 | 25.4262 | 20.6021 | 12.9534 | 13.9118 | 7.0709 | 9.5413 | 21.0619 | 16.2305 | 10.523 | 8.3796 | 10.1095 | 12.2376 | 12.0977
Forecast Demand 2026 10% POE (MW) | 61.4375 | 44.332 | 61.5156 | 124.2514 | 74.8521 | 118.5447 | 6.2621 | 93.2564 | 19.9809 | 32.7525 | 71.6826 | 32.0938 | 20.3389 | 16.7614 | 8.1595 | 76.597 | 79.8845 | 41.6976 | 82.7816 | 48.8534 | 74.042 | 57.1573 | 86.3878 | 54.0552 | 34.7031 | 41.8699 | 13.6786 | 13.9386 | 14.215 | 12.981 | 27.0018 | 17.1356 | 14.3183 | 13.9293 | 17.3125 | 13.6077 | 15.4966 | 16.9735 | 16.4464 | 15.223 | 13.2644 | 10.8055 | 16.0804 | 24.8097 | 16.1667 | 13.3123 | 10.786 | 11.1968 | 15.793 | 15.9369 | 12.2925 | 12.8083 | 13.3727 | 29.8793 | 25.6895 | 14.3351 | 7.7217 | 9.2387 | 12.6208 | 18.714 | 15.7583 | 24.637 | 18.5672 | 14.7131 | 15.2566 | 6.8956 | 10.59 | 16.8958 | 17.1679 | 11.5225 | 9.3145 | 11.2093 | 11.695 | 12.5072
Forecast Demand 2027 10% POE (MW) | 62.4432 | 44.1775 | 62.1532 | 128.0364 | 74.9606 | 121.4869 | 6.2479 | 101.4192 | 20.3349 | 32.6947 | 71.8736 | 32.1259 | 20.2914 | 16.7295 | 8.2072 | 81.5678 | 79.6008 | 41.5127 | 82.7373 | 51.9995 | 73.7998 | 56.8046 | 88.5516 | 53.9533 | 34.3264 | 42.5889 | 13.6786 | 13.8513 | 14.1979 | 13.3195 | 29.7944 | 17.9696 | 14.6169 | 14.0591 | 17.8225 | 14.5007 | 15.5496 | 16.8275 | 16.792 | 15.7131 | 13.3425 | 10.8049 | 16.4811 | 26.075 | 20.885 | 15.5725 | 10.7492 | 11.5451 | 17.203 | 16.7089 | 12.3314 | 12.7748 | 13.3877 | 34.1265 | 27.3804 | 14.6504 | 7.7313 | 9.2223 | 14.0665 | 20.9628 | 15.8624 | 24.6203 | 19.0735 | 14.6692 | 15.2137 | 6.9939 | 10.6929 | 17.4874 | 17.2788 | 11.5427 | 9.2264 | 11.2192 | 12.1823 | 12.8659
Forecast Demand 2028 10% POE (MW) | 62.852 | 44.8682 | 63.0168 | 131.3686 | 75.3455 | 119.8786 | 6.2632 | 117.1415 | 20.7308 | 32.7326 | 71.9623 | 32.2551 | 20.2507 | 16.7673 | 8.2614 | 84.5283 | 79.5894 | 41.4114 | 83.1283 | 51.8908 | 73.5558 | 57.6231 | 93.901 | 53.9795 | 34.0788 | 42.5369 | 13.6266 | 13.7808 | 14.2117 | 13.7042 | 32.8405 | 18.789 | 14.9604 | 14.1989 | 18.3844 | 15.3485 | 21.1974 | 16.7039 | 17.2539 | 16.4149 | 13.4031 | 10.8412 | 17.0233 | 27.3676 | 24.3807 | 16.4535 | 10.7239 | 11.9739 | 18.6976 | 18.0397 | 12.3317 | 12.7615 | 13.4193 | 45.8931 | 29.1732 | 15.079 | 7.7212 | 9.257 | 15.4985 | 22.6913 | 16.0331 | 24.3541 | 20.913 | 14.6532 | 15.1816 | 7.1026 | 10.8425 | 22.1191 | 17.4055 | 11.5772 | 9.1757 | 11.2033 | 12.6449 | 13.1452
Forecast Demand 2029 10% POE (MW) | 63.5363 | 44.3728 | 64.3971 | 136.7682 | 75.8529 | 121.9204 | 6.3353 | 125.0852 | 21.0006 | 32.8504 | 73.1751 | 32.6072 | 20.3293 | 16.8847 | 8.367 | 86.8984 | 80.0199 | 41.7033 | 84.734 | 52.1789 | 74.3014 | 57.1803 | 94.1801 | 54.1665 | 34.1141 | 43.1408 | 13.7223 | 13.7867 | 14.3141 | 14.3216 | 36.3853 | 19.6776 | 15.3502 | 14.435 | 19.0376 | 16.4204 | 21.2436 | 16.6471 | 17.6146 | 17.1309 | 13.561 | 10.9312 | 17.5277 | 28.8001 | 27.7921 | 18.084 | 10.6944 | 12.3835 | 20.1342 | 19.2417 | 12.4521 | 12.7699 | 13.5216 | 50.2549 | 30.9738 | 15.4822 | 7.7572 | 9.3115 | 17.0047 | 23.7065 | 16.3638 | 24.488 | 21.0159 | 14.6721 | 15.1657 | 7.2442 | 10.9741 | 22.0357 | 17.6669 | 11.707 | 9.1821 | 11.2847 | 13.2213 | 13.5851
Forecast Demand 2030 10% POE (MW) | 64.6459 | 44.8257 | 69.1887 | 141.634 | 77.0208 | 124.6444 | 6.448 | 134.2135 | 21.2206 | 33.2507 | 75.3957 | 34.0628 | 20.4863 | 17.1864 | 8.6545 | 88.8048 | 81.1895 | 42.7147 | 88.1963 | 52.5641 | 75.2694 | 58.4593 | 96.2592 | 54.5455 | 34.6881 | 44.2401 | 13.8253 | 14.5034 | 14.812 | 15.6324 | 39.1913 | 20.7903 | 15.7305 | 14.6965 | 19.7239 | 17.4408 | 21.4085 | 16.5955 | 18.1619 | 18.0108 | 13.7564 | 11.0677 | 18.0764 | 30.2174 | 31.1077 | 19.7003 | 10.7036 | 12.8241 | 21.4503 | 20.4263 | 12.6266 | 12.8257 | 13.9317 | 55.9901 | 32.9336 | 16.1282 | 7.9339 | 9.3689 | 18.6227 | 24.0253 | 16.6244 | 25.642 | 20.9636 | 14.8043 | 15.1891 | 7.453 | 11.1848 | 22.0149 | 17.9495 | 11.8632 | 9.3316 | 11.323 | 13.8637 | 14.0123
Forecast Demand 2026 50% POE (MW) | 54.5838 | 40.5667 | 54.5438 | 108.3435 | 64.8074 | 101.6723 | 5.4965 | 77.1559 | 18.8359 | 30.1529 | 64.3066 | 28.9453 | 17.2373 | 13.9843 | 7.7996 | 68.9791 | 74.1527 | 37.143 | 75.5604 | 43.789 | 63.849 | 50.7122 | 78.7351 | 44.4693 | 30.7665 | 37.7094 | 12.5924 | 13.1895 | 13.0075 | 12.102 | 21.747 | 14.6145 | 12.4548 | 12.7859 | 15.8992 | 10.251 | 13.7375 | 16.0015 | 14.1259 | 13.4893 | 11.606 | 8.6289 | 13.5407 | 22.4024 | 12.5933 | 11.9263 | 9.3759 | 8.6452 | 12.8384 | 15.1154 | 10.7192 | 11.7181 | 11.7588 | 25.2995 | 22.6808 | 12.6985 | 6.6517 | 7.8466 | 9.5061 | 16.6805 | 13.6559 | 23.8895 | 17.8663 | 12.7065 | 13.9217 | 6.4701 | 9.1351 | 15.7484 | 15.5156 | 10.3291 | 8.2809 | 10.0058 | 10.216 | 10.8021
Forecast Demand 2027 50% POE (MW) | 55.5843 | 40.3583 | 54.8535 | 111.4611 | 64.4918 | 104.4042 | 5.555 | 83.8722 | 19.2754 | 30.1204 | 64.9347 | 29.2257 | 17.1909 | 13.8965 | 7.8426 | 74.0072 | 73.9998 | 37.1166 | 75.9343 | 46.8837 | 63.869 | 50.3316 | 80.959 | 44.3184 | 30.6124 | 38.0299 | 12.552 | 13.0878 | 12.9616 | 12.5832 | 24.5067 | 15.372 | 12.7299 | 12.8648 | 16.2956 | 10.8988 | 13.782 | 15.8485 | 14.4563 | 13.9214 | 11.6321 | 8.6496 | 13.9185 | 23.5885 | 16.8423 | 14.4219 | 9.3175 | 8.9551 | 14.1565 | 15.7145 | 10.6503 | 11.6616 | 11.8097 | 29.3274 | 24.2143 | 12.9884 | 6.6254 | 7.8299 | 10.9367 | 18.9219 | 13.7668 | 23.8639 | 18.6839 | 12.6776 | 13.9021 | 6.5659 | 9.1803 | 16.4136 | 15.6128 | 10.3196 | 8.2988 | 9.991 | 10.6445 | 11.0668
Forecast Demand 2028 50% POE (MW) | 55.7239 | 40.5152 | 56.1073 | 115.2173 | 64.501 | 102.6031 | 5.5468 | 98.6703 | 19.7019 | 30.0912 | 65.0474 | 29.003 | 17.2767 | 13.963 | 7.8964 | 76.6284 | 73.965 | 36.8817 | 75.4202 | 46.9038 | 63.9809 | 50.2616 | 86.1771 | 44.4619 | 30.4603 | 38.3363 | 12.6141 | 13.1768 | 12.9109 | 12.957 | 27.2562 | 16.1765 | 13.0604 | 13.0447 | 16.8086 | 11.6921 | 19.3094 | 15.758 | 14.7349 | 14.4121 | 11.7183 | 8.7303 | 14.415 | 24.694 | 19.966 | 15.205 | 9.2708 | 9.2472 | 15.585 | 16.9517 | 10.7564 | 11.6095 | 11.7304 | 40.0999 | 25.6998 | 13.3677 | 6.6211 | 7.803 | 12.2666 | 20.6773 | 13.9037 | 24.1226 | 19.9605 | 12.6551 | 13.8693 | 6.6686 | 9.2913 | 21.0391 | 15.7601 | 10.3248 | 8.1762 | 10.0197 | 11.085 | 11.438
Forecast Demand 2029 50% POE (MW) | 55.9731 | 40.7067 | 57.4547 | 119.0984 | 64.973 | 105.5757 | 5.5919 | 105.7938 | 19.9995 | 30.5591 | 65.9643 | 30.0735 | 17.3524 | 14.0369 | 8.0277 | 78.9811 | 74.4648 | 37.1956 | 77.012 | 47.1158 | 64.4831 | 50.6728 | 86.5928 | 44.5209 | 30.4336 | 38.9966 | 12.6208 | 13.281 | 13.0356 | 14.0212 | 30.0067 | 17.0262 | 13.4429 | 13.1681 | 17.4074 | 12.4587 | 19.3701 | 15.6791 | 15.0401 | 15.1138 | 11.9001 | 8.757 | 14.8035 | 25.9455 | 23.02 | 16.4532 | 9.2438 | 9.6034 | 16.9327 | 18.1071 | 10.8254 | 11.6457 | 12.1914 | 43.8359 | 27.3813 | 13.7363 | 6.6562 | 7.8414 | 13.7227 | 21.6109 | 14.0561 | 24.4712 | 19.9525 | 12.7132 | 13.8693 | 6.8057 | 9.4244 | 20.9673 | 15.9167 | 10.4322 | 8.1653 | 10.0619 | 11.5641 | 11.7046
Forecast Demand 2030 50% POE (MW) | 57.6926 | 40.861 | 60.6407 | 123.2461 | 65.1637 | 106.371 | 5.7232 | 114.415 | 20.0798 | 31.2459 | 67.502 | 32.3185 | 17.5414 | 14.3041 | 8.3207 | 80.4506 | 75.0153 | 37.8757 | 80.381 | 47.5921 | 65.603 | 52.3768 | 89.3338 | 44.7099 | 30.6516 | 40.1266 | 12.8699 | 13.707 | 13.4273 | 14.6598 | 32.5722 | 17.8251 | 13.7623 | 13.387 | 17.9848 | 13.4205 | 19.5174 | 15.6334 | 15.4191 | 15.8525 | 12.0389 | 8.8657 | 15.3211 | 27.2421 | 26.0683 | 18.0695 | 9.2898 | 9.9586 | 18.1655 | 19.3347 | 10.9884 | 11.6173 | 12.0362 | 50.2651 | 29.1508 | 14.261 | 6.6964 | 7.9822 | 15.2322 | 21.9368 | 14.2567 | 24.9177 | 19.984 | 12.8239 | 13.9118 | 7.0002 | 9.5413 | 21.0619 | 16.2305 | 10.523 | 8.2958 | 10.1095 | 12.2376 | 12.0977
Voltage level | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
Maximum Load at risk 2026 (N-1 for ZSS , N for Feeder's) | -24.8025 | 13.939 | -3.9484 | 35.0514 | 25.3521 | 30.7447 | -0.69388 | 44.6474 | -9.7131 | 32.7525 | -17.5164 | 0.69378 | 2.2389 | 3.3614 | 0.88448 | 31.397 | 34.8845 | 13.6976 | 24.1816 | 0.6404 | -25.948 | 20.3293 | 11.5438 | 19.1082 | -11.4969 | -2.1301 | 2.9272 | 2.4156 | 2.4451 | 3.1041 | 12.7124 | 4.0274 | 1.9341 | 0.97356 | 3.1659 | 0.49958 | 1.2072 | 3.3928 | 0.17555 | 2.4578 | 0.84217 | 1.0727 | 3.1247 | 10.9014 | 1.5674 | -0.26838 | 1.355 | 0.33685 | 1.6362 | 3.0002 | 0.10761 | 0.35932 | 1.4519 | 15.3612 | 11.1714 | 0.045668 | 0.99996 | 0.47449 | -1.0971 | 4.9962 | 1.4689 | 12.1271 | 4.7065 | 1.6983 | 1.9198 | 0.10531 | -0.079462 | 4.5116 | 3.2596 | 0.66257 | 1.3547 | 0.34938 | 0.64451 | 2.5999
Maximum Load at risk 2027 (N-1 for ZSS , N for Feeder's) | -23.7968 | 13.7845 | -3.3108 | 38.8364 | 25.4606 | 33.6869 | -0.70805 | 52.8102 | -9.3591 | 32.6947 | -17.3254 | 0.7259 | 2.1914 | 3.3295 | 0.93218 | 36.3678 | 34.6008 | 13.5127 | 24.1373 | 3.7865 | -26.1902 | 19.9766 | 13.7076 | 19.0063 | -11.8736 | -1.4111 | 2.9273 | 2.3283 | 2.428 | 3.4427 | 15.505 | 4.8614 | 2.2328 | 1.1034 | 3.6759 | 1.3926 | 1.2602 | 3.2469 | 0.52111 | 2.9479 | 0.92022 | 1.0721 | 3.5253 | 12.1666 | 6.2858 | 1.9918 | 1.3182 | 0.6851 | 3.0462 | 3.7722 | 0.14648 | 0.32588 | 1.4669 | 19.6085 | 12.8623 | 0.36094 | 1.0095 | 0.45816 | 0.34861 | 7.245 | 1.573 | 12.1104 | 5.2128 | 1.6544 | 1.8769 | 0.20361 | 0.023495 | 5.1032 | 3.3704 | 0.68269 | 1.2666 | 0.3592 | 1.1318 | 2.9586
Maximum Load at risk 2028 (N-1 for ZSS , N for Feeder's) | -23.388 | 14.4752 | -2.4472 | 42.1686 | 25.8455 | 32.0786 | -0.69281 | 68.5325 | -8.9632 | 32.7326 | -17.2367 | 0.85513 | 2.1507 | 3.3673 | 0.98642 | 39.3283 | 34.5894 | 13.4114 | 24.5283 | 3.6778 | -26.4342 | 20.7951 | 19.057 | 19.0325 | -12.1212 | -1.4631 | 2.8753 | 2.2578 | 2.4418 | 3.8273 | 18.5511 | 5.6808 | 2.5762 | 1.2431 | 4.2379 | 2.2404 | 6.908 | 3.1232 | 0.98306 | 3.6497 | 0.98083 | 1.1084 | 4.0676 | 13.4593 | 9.7815 | 2.8729 | 1.2929 | 1.1139 | 4.5408 | 5.103 | 0.14681 | 0.31255 | 1.4985 | 31.3751 | 14.6551 | 0.78962 | 0.99949 | 0.49279 | 1.7806 | 8.9734 | 1.7437 | 11.8442 | 7.0522 | 1.6384 | 1.8449 | 0.31223 | 0.17311 | 9.735 | 3.4971 | 0.71719 | 1.2159 | 0.34336 | 1.5944 | 3.2379
Maximum Load at risk 2029 (N-1 for ZSS , N for Feeder's) | -22.7037 | 13.9798 | -1.0669 | 47.5682 | 26.3529 | 34.1204 | -0.6207 | 76.4762 | -8.6934 | 32.8504 | -16.0239 | 1.2072 | 2.2293 | 3.4847 | 1.092 | 41.6984 | 35.0199 | 13.7033 | 26.134 | 3.9659 | -25.6886 | 20.3523 | 19.3361 | 19.2195 | -12.0859 | -0.8592 | 2.9709 | 2.2637 | 2.5442 | 4.4447 | 22.0959 | 6.5695 | 2.966 | 1.4793 | 4.8911 | 3.3123 | 6.9541 | 3.0665 | 1.3437 | 4.3656 | 1.1388 | 1.1984 | 4.5719 | 14.8917 | 13.1929 | 4.5033 | 1.2634 | 1.5236 | 5.9774 | 6.305 | 0.26718 | 0.32097 | 1.6008 | 35.7368 | 16.4557 | 1.1928 | 1.0354 | 0.5473 | 3.2869 | 9.9887 | 2.0744 | 11.9781 | 7.1552 | 1.6573 | 1.8289 | 0.45388 | 0.30467 | 9.6515 | 3.7585 | 0.84703 | 1.2224 | 0.42476 | 2.1708 | 3.6777
Maximum Load at risk 2030 (N-1 for ZSS , N for Feeder's) | -21.5941 | 14.4327 | 3.7247 | 52.434 | 27.5208 | 36.8444 | -0.50798 | 85.6045 | -8.4734 | 33.2507 | -13.8033 | 2.6628 | 2.3863 | 3.7864 | 1.3795 | 43.6048 | 36.1895 | 14.7147 | 29.5963 | 4.3511 | -24.7206 | 21.6313 | 21.4152 | 19.5985 | -11.5119 | 0.24009 | 3.074 | 2.9804 | 3.0421 | 5.7555 | 24.9019 | 7.6822 | 3.3463 | 1.7408 | 5.5773 | 4.3326 | 7.1191 | 3.0149 | 1.891 | 5.2456 | 1.3341 | 1.3349 | 5.1207 | 16.309 | 16.5085 | 6.1197 | 1.2726 | 1.9642 | 7.2935 | 7.4896 | 0.4417 | 0.3768 | 2.0108 | 41.472 | 18.4155 | 1.8388 | 1.2122 | 0.60476 | 4.9049 | 10.3074 | 2.335 | 13.1321 | 7.1028 | 1.7895 | 1.8523 | 0.66267 | 0.51533 | 9.6308 | 4.0412 | 1.0032 | 1.3718 | 0.463 | 2.8132 | 4.105
Energy at risk 2026 (Total N, N-1,N-2) | 0.00021204 | 3.9505 | 0.00091895 | 0 | 0.11488 | 1.185 | 0.00010573 | 0.3 | 0.15945 | 52.836 | 0.00040374 | 0.014612 | 0.67651 | 0.65418 | 1.6122 | 0.67612 | 0.18366 | 0.038289 | 0.47213 | 0.001286 | 0.00090922 | 1.5368 | 0.29744 | 7.6259 | 1.3516 | 0 | 36.6 | 0 | 0.2 | 26.5 | 3.9 | 2.1 | 0.4 | 0 | 7.5 | 0 | 0 | 7 | 0 | 6 | 0 | 1 | 5.5 | 79.6 | 0 | 0 | 1.9 | 0 | 51.7 | 197.6 | 0 | 0 | 1.7 | 10.6 | 5.1 | 0 | 0.5 | 1.8 | 0 | 1.8 | 0.4 | 1664.8 | 0.1 | 1.3 | 6.2 | 0 | 0 | 11.1 | 3.7 | 1.4 | 0.1 | 0.1 | 4.8 | 20.8513
Energy at risk 2027 (Total N, N-1,N-2) | 0.00029706 | 4.2477 | 0.0020435 | 0 | 0.14703 | 3.1184 | 0.00017649 | 1 | 0.18955 | 67.8285 | 0.0006763 | 0.043359 | 0.7346 | 0.71257 | 1.8001 | 1.7338 | 0.45136 | 0.044257 | 0.60254 | 0.0015932 | 0.0011139 | 1.8256 | 0.8212 | 8.7434 | 1.5069 | 0 | 39 | 0 | 0.8 | 80 | 61.3 | 10.8 | 1 | 0 | 22.7 | 0 | 0 | 6 | 0 | 13.8 | 0 | 1 | 9.1 | 2686.9 | 42.2 | 0.3 | 1.7 | 0 | 385.3 | 181.5 | 0 | 0 | 1.1 | 289.4 | 54.5 | 0 | 0.6 | 1.4 | 0 | 248.1 | 2.2 | 6222.6 | 40.6 | 1.4 | 7.4 | 0 | 0 | 0 | 6.8 | 1.6 | 0.1 | 0.1 | 29.7 | 2.2444
Energy at risk 2028 (Total N, N-1,N-2) | 0.00051765 | 4.4115 | 0.0035363 | 0 | 0.1788 | 4.3513 | 0.00028013 | 2.1 | 0.22415 | 74.5681 | 0.00091212 | 0.056846 | 0.7918 | 0.75951 | 1.9471 | 3.3659 | 0.56917 | 0.048268 | 0.70422 | 0.0050476 | 0.0012387 | 1.8639 | 1.3751 | 9.1217 | 1.6634 | 0 | 38.8 | 0 | 1.2 | 129.4 | 205.1 | 55.3 | 1.2 | 0 | 51.1 | 0 | 0 | 4.3 | 0.1 | 40.4 | 0 | 0.8 | 11.5 | 4251.9 | 858.5 | 157.2 | 1.3 | 0.1 | 927.2 | 564.7 | 0 | 0 | 1.3 | 3188.4 | 392.4 | 0 | 0.5 | 0.9 | 0 | 731 | 3.1 | 6483.9 | 135.6 | 1.2 | 7.1 | 0 | 0 | 0.6 | 6.6 | 1.3 | 0 | 0 | 93.7 | 5.2779
Energy at risk 2029 (Total N, N-1,N-2) | 0.00065917 | 5.0772 | 0.0062939 | 0 | 0.21873 | 4.0836 | 0.00043301 | 8.3 | 0.2637 | 81.7725 | 0.0011313 | 0.063903 | 0.85692 | 0.82112 | 2.1078 | 4.9833 | 0.71572 | 0.050395 | 0.78026 | 0.0056326 | 0.0013199 | 2.144 | 4.0395 | 10.0857 | 1.8343 | 0 | 38.5 | 0 | 1.1 | 180.8 | 510.6 | 588.8 | 1.6 | 0 | 109.5 | 0 | 27.1 | 3.3 | 0.2 | 120.6 | 0 | 0.7 | 15.9 | 5778.3 | 3369.8 | 655.9 | 1.1 | 0.3 | 1815.1 | 1274.7 | 0 | 0 | 3.2 | 24996 | 1077.7 | 0.2 | 0.4 | 0.6 | 2.2 | 1313.1 | 4.5 | 7646.2 | 350.7 | 1.1 | 6.8 | 0 | 0 | 332.3 | 6.7 | 1.1 | 0 | 0 | 205.5 | 8.7279
Energy at risk 2030 (Total N, N-1,N-2) | 0.00090497 | 5.0623 | 0.012694 | 0 | 0.2694 | 5.5437 | 0.0006429 | 16.2 | 0.30685 | 90.4247 | 0.0021617 | 0.10984 | 0.92884 | 0.89624 | 2.3112 | 6.9809 | 0.94266 | 0.061253 | 1.1202 | 0.0070953 | 0.0021142 | 2.3132 | 4.6787 | 10.97 | 2.0296 | 0 | 42.1 | 0 | 1.3 | 261.3 | 1249.1 | 1838.2 | 2.2 | 0 | 196.2 | 2.6 | 31.1 | 2.9 | 0.4 | 286.3 | 0 | 0.8 | 20.7 | 7594.8 | 9816.6 | 1315.8 | 0.9 | 0.7 | 2974 | 2354.9 | 0 | 0 | 2.9 | 44013.5 | 2291.5 | 0.4 | 0.4 | 0.5 | 14.1 | 1714.8 | 7.2 | 9100.1 | 383.7 | 1.1 | 6.7 | 0 | 0 | 300.1 | 8.2 | 1.3 | 0 | 0 | 664 | 16.4015
Limitation Timing | N/A | N/A | N/A | 2025-12-01 | 2025-12-01 | 2025-12-01 | N/A | 2025-12-01 | N/A | 2026-12-01 | N/A | TBC | 2026-12-01 | 2026-12-01 | N/A | 2026-12-01 | 2026-12-01 | N/A | N/A | N/A | N/A | TBC | N/A | 2029-12-01 | TBC | TBC | 2025-12-01 | 2026-12-01 | 2025-12-01 | 2026-12-01 | 2025-12-01 | 2025-12-01 | 2025-12-01 | 2026-12-01 | 2026-12-01 | 2026-12-01 | 2026-12-01 | 2026-12-01 | 2025-12-01 | 2026-12-01 | 2026-12-01 | 2026-12-01 | 2025-12-01 | 2025-12-01 | 2025-12-01 | 2027-12-01 | 2026-12-01 | 2026-12-01 | 2026-12-01 | 2026-12-01 | 2026-12-01 | 2026-12-01 | 2026-12-01 | 2024-12-01 | 2024-12-01 | 2026-12-01 | 2025-12-01 | 2025-12-01 | 2027-12-01 | 2026-12-01 | 2026-12-01 | 2025-12-01 | 2025-12-01 | 2025-12-01 | 2026-12-01 | 2026-12-01 | 2027-12-01 | 2025-12-01 | 2026-12-01 | 2025-12-01 | 2025-12-01 | 2025-12-01 | 2026-12-01 | 2025-12-01
Preferred network investment | Bairnsdale REFCL Augmentation | Benalla Zone Substation rebuild and REFCL installation | Bayswater Zone Substation rebuild | Clyde North Zone Substation Capacity Augmentation | ZSS Can be risk managed until 2028 No-network solutions will be considered | Wollert Zone Substation Development Project | REFCL Driven Augmentation | Beveridge Zone Substation Development Project | Kilmore South Zone Substation rebuild | ZSS Can be risk managed until 2028 No-network solutions will be considered | REFCL Lilydale Zone substation | Maffra Zone Substation rebuild | ZSS Can be risk managed until 2028 No-network solutions will be considered | ZSS Can be risk managed until 2028 No-network solutions will be considered | Newmerella Zone Substation rebuild | Pakenham South New Zone Substation | Pakenham South New Zone Substation | REFCL Driven Augmentation | Thomastown Zone Substation rebuild | Traralgon Zone Substation rebuild | Watsonia Zone Substation rebuild | ZSS Can be risk managed until 2028 No-network solutions will be considered | Warragul Zone Substation rebuild | Wonthaggi Zone Substation Upgrade | REFCL Driven Augmentation | REFCL Driven Augmentation | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Install a new 22kV distribution feeder (CLN33) | Install a new 22kV distribution feeder (CLN32) | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Pakenham South Zone Substation Development | Pakenham South Zone Substation Development | Construct a new 22kV distribution feeder at Cranbourne Zone Substation (CRE34) | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Install a new 22kV distribution feeder (CLN32) | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Wollert Zone Substation Development Project | Wollert Zone Substation Development Project | Wollert Zone Substation Development Project | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Wollert Zone Substation Development Project | Wollert Zone Substation Development Project | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Beveridge Zone Substation Development Project | Beveridge Zone Substation Development Project | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Pakenham South Zone Substation Development | Pakenham South Zone Substation Development | Pakenham South Zone Substation Development | Pakenham South Zone Substation Development | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Baw Baw Shire (New 22kV Feeder WGL31 & New Switchboard at WGL ZSS) | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Feeder can be risk managed until 2028. Non-network solutions will be considered. | Install a new 22kV distribution feeder (WOTS21)
Preferred network investment capital cost | 23250000 | 16700000 | 16050000 | 28100000 | TBC | 78953037 | 21009328 | 110410835 | 9360000 | TBC | 24040000 | 35100000 | TBC | TBC | 19657000 | 69756373 | 69756373 | 21009328 | 48124000 | 18663000 | 43962000 | TBC | 31000000 | 10115917 | 21009328 | 42018656 | TBC | TBC | TBC | TBC | 5085199 | 16668250 | TBC | TBC | 69756373 | 69756373 | 7911704 | TBC | TBC | 16668250 | TBC | TBC | TBC | 78953037 | 78953037 | 78953037 | TBC | TBC | 78953037 | 78953037 | TBC | TBC | TBC | 110410835 | 110410835 | TBC | TBC | TBC | TBC | 69756373 | 69756373 | 69756373 | 69756373 | TBC | TBC | TBC | TBC | 29798283 | TBC | TBC | TBC | TBC | TBC | 5706861
Preferred annual network investment operating cost | 232500 | 167000 | 160500 | 281000 | N/A | 789530.37 | 210093.28 | 1104108.35 | 93600 | TBC | 240400 | 351000 | TBC | TBC | 196570 | 697563.73 | 697563.73 | 210093.28 | 481240 | 186630 | 439620 | TBC | 310000 | 101159.17 | 210093.28 | 420186.56 | TBC | TBC | TBC | TBC | 50851.99 | 166682.5 | TBC | TBC | 697563.73 | 697563.73 | 79117.04 | TBC | TBC | 166682.5 | TBC | TBC | TBC | 789530.37 | 789530.37 | 789530.37 | TBC | TBC | 789530.37 | 789530.37 | TBC | TBC | TBC | 1104108.35 | 1104108.35 | TBC | TBC | TBC | TBC | 697563.73 | 697563.73 | 697563.73 | 697563.73 | TBC | TBC | TBC | TBC | 297982.83 | TBC | TBC | TBC | TBC | TBC | 57068.61
Preferred network investment cost accuracy | 0.3 | 0.3 | 0.3 | 0.3 | N/A | 0.3 | 0.3 | 0.3 | 0.3 | N/A | 0.3 | 0.3 | N/A | N/A | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | N/A | 0.3 | 0.3 | 0.3 | 0.3 | N/A | N/A | N/A | N/A | 0.3 | 0.3 | N/A | N/A | 0.3 | 0.3 | 0.3 | N/A | N/A | 0.3 | N/A | N/A | N/A | 0.3 | 0.3 | 0.3 | N/A | N/A | 0.3 | 0.3 | N/A | N/A | N/A | 0.3 | 0.3 | N/A | N/A | N/A | N/A | 0.3 | 0.3 | 0.3 | 0.3 | N/A | N/A | N/A | N/A | 0.3 | N/A | N/A | N/A | N/A | N/A | 0.3
Preferred network investment cost accuracy | 0.3 | 0.3 | 0.3 | 0.3 | N/A | 0.3 | 0.3 | 0.3 | 0.3 | N/A | 0.3 | 0.3 | N/A | N/A | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | N/A | 0.3 | 0.3 | 0.3 | 0.3 | N/A | N/A | N/A | N/A | 0.3 | 0.3 | N/A | N/A | 0.3 | 0.3 | 0.3 | N/A | N/A | 0.3 | N/A | N/A | N/A | 0.3 | 0.3 | 0.3 | N/A | N/A | 0.3 | 0.3 | N/A | N/A | N/A | 0.3 | 0.3 | N/A | N/A | N/A | N/A | 0.3 | 0.3 | 0.3 | 0.3 | N/A | N/A | N/A | N/A | 0.3 | N/A | N/A | N/A | N/A | N/A | 0.3
Proposed timing | 2027-12-01 | 2026-06-01 | 2028-12-01 | 2025-12-01 | TBC | 2028-12-01 | TBC | 2026-12-01 | 2026-12-01 | TBC | 2027-12-01 | 2025-12-01 | TBC | TBC | 2026-12-01 | 2028-12-01 | 2028-12-01 | TBC | Stage 1 2026 , Stage 2 2030 | Stage 1 2026 , Stage 2 2030 | TBC | TBC | 2026-10-01 | 2030-12-01 | TBC | TBC | TBC | TBC | TBC | TBC | 2026-12-01 | TBC | TBC | TBC | 2028-12-01 | 2028-12-01 | 2029-12-01 | TBC | TBC | 2029-12-01 | TBC | TBC | TBC | 2028-12-01 | 2028-12-01 | 2028-12-01 | TBC | TBC | 2028-12-01 | 2028-12-01 | TBC | TBC | TBC | 2026-12-01 | 2026-12-01 | TBC | TBC | TBC | TBC | 2028-12-01 | 2028-12-01 | 2028-12-01 | 2028-12-01 | N/A | N/A | N/A | N/A | 2029-12-01 | N/A | N/A | N/A | N/A | N/A | 2030-12-01
Demand reduction required to defer investment by 1 year | N/A | N/A | N/A | N/A | 25.3521 | 30.7447 | N/A | 44.6474 | -17.77 | 32.6947 | -85.97 | 0.69378 | 2.1507 | 3.3295 | 0.88448 | 31.397 | 34.5894 | N/A | 24.1373 | 0.6404 | -26.4342 | 19.9766 | 11.5438 | 19.0063 | N/A | N/A | 2.8753 | 2.2578 | 2.428 | 3.1041 | 12.7124 | 4.0274 | 1.9341 | 0.97356 | 3.1659 | 0.49958 | 1.2072 | 3.0149 | 0.17555 | 2.4578 | 0.84217 | 1.0721 | 3.1247 | 10.9014 | 1.5674 | -0.26838 | 1.2634 | 0.33685 | 1.6362 | 3.0002 | 0.10761 | 0.31255 | 1.4519 | 15.3612 | 11.1714 | 0.045668 | 0.99949 | 0.45816 | -1.0971 | 4.9962 | 1.4689 | 11.8442 | 4.7065 | 1.6384 | 1.8289 | 0.10531 | -0.079462 | 4.5116 | 3.2596 | 0.66257 | 1.2159 | 0.34336 | 0.64451 | 2.5999
Annual Deferral Value | N/A | N/A | TBC | N/A | TBC | 5300000 | N/A | 7700000 | 630000 | TBC | N/A | N/A | TBC | TBC |  | 4664322.9 | 4664322.9 | N/A |  |  |  | TBC | N/A | 726072 | N/A | N/A | TBC | TBC | TBC | TBC | 1527409 | 1527409 | TBC | TBC | 4664322.9 | 4664322.9 | 552764 | TBC | TBC | 1527409 | TBC | TBC | TBC | 5300000 | 5300000 | 5300000 | TBC | TBC | 5300000 | 5300000 | TBC | TBC | TBC | 7700000 | 7700000 | TBC | TBC | TBC | TBC | 4664322.9 | 4664322.9 | 4664322.9 | 4664322.9 | TBC | TBC | TBC | TBC | 1778798 | TBC | TBC | TBC | TBC | TBC | 336808
Load transfer capability | 0 | 1.6 | 24 | 0 | 8 | 14.1 | 1 | 0 | 0 | 0 | 17.7 | 6.5 | 0 | 0 | 3.2 | 0 | 1.7 | 0 | 20.7 | 9.7 | 20.6 | 2.3 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 3 | 0 | 3 | 3 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.5 | 0 | 1.4 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency generation | - | - | - | - | - | - | - | 12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Historic use of existing emergency response | - | 12/10/2024: 2.5MVA | - | - | - | - | - | 15/12/2024: 3.1MVA 2/12/2025: 1.8MVA 24/12/2024: 0.5MVA 24/12/2024: 0.32MVA 31/1/2025: 0.85MVA 0/1/1900: MVA 13/12/2024: 0.9MVA 14/12/2024: 2.2MVA | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -